## Summary of HIRA
Summary of HIRA
|  | VEDANTA LIMITED – VALUE ADDED BUSINESS |  | Format No.: | FRMT/MR/22 |  |  |  |  | Trivial | 1-2 |  |  | Department Use only
[10 empty] | Acceptable | 3-4 |  |  | Dept | Electrical
|  | INTEGRATED MANAGEMENT SYSTEM |  | Revision Date: | 04.04.2022 |  |  |  |  | Moderate | 5-9 |  |  | Unit | PID-1
|  | RISK ASSESSMENT AND RISK CONTROL |  | Revision No.: | 2 |  |  |  |  | Substantial | 10-16 |  |  | Review Date | 04.03.2023
|  |  |  | Page No.: | 1 of 1 | RISK LEVEL WITH EXISTING CONTROL |  |  |  | Intolerable | 20-25 | RISK LEVEL AFTER OPPORTUNITIES IMPLEMENTATION
SL no: | Activity | Types of Hazards | HAZARDS | RISK | PERSONNELS AT RISK | EXISTING CONTROL MEASURES | LIKELY HOOD OF HARM | SEVERITY OF HARM | RISK LEVEL | OPPORTUNITIES (PROPOSED CONTROL MEASURES,IF ANY) | Responsibity for Implementing the Opportunity Idenfied | STATUS | REVISED LIKELY HOOD OF HARM | REVISED SEVERITY OF HARM | REVISED RISK LEVEL
1 | HT Motor overhauling | Physical | Noise | hearing impairment | Elect. Engr,Electrician, Fitter and contract workmen | Use of ear plug | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
2 | HT Motor overhauling | Chemical | Fumes and vapours | Burn Injury | Elect. Engr,Electrician, Fitter and contract workmen | Use of Nose mask and Goggles | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
3 | HT Motor overhauling | Mechanical | Falling | personal injury | Elect. Engr,Electrician, Fitter and contract workmen | Training of employees, Work instruction | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3 | COMPLETED
4 | HT Motor overhauling | Behavioural Hazard | Hazard due Human Behaviour Like non usage of PPE. Hazard due to Human error like non following of WI. | personal injury | Elect. Engr,Electrician, Fitter and contract workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4 | IN PROGRESS
5 | HT Motor overhauling | Behavioural Hazard | Strain while handling equipment | personal injury | Electrician, Fitter and contract workmen | Use of handling tools and tackles like motor lifting rod, chain pulley crane, trolley. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4 | PENDING
6 | Motor Replacement | Mechnical | Falling | personal injury | Electrician,Fitter and contract employee | Use of special motor lifting rod. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
7 | Motor Replacement | Physical | Noise | hearing impairment | Elect. Engr,Electrician, Fitter and contact workmen | Use of ear plug | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
8 | Motor Replacement | Behavioural Hazard | Hazard due Human Behaviour use of simple rod. Human error like improper usage of lifting rod. | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
9 | Motor Replacement | Mechanical | Trapping/hitting while shifting the motor in vehicle | personal injury | Electrician, Fitter and contact workmen | Work instruction | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
10 | Routine Maintenance of Electrical feeder | Physical | Electrical shock/ Burns | Burn Injury | Electrical Engineer,Electrician and contract employee | Traing of employee, Work instruction, electrical shutdown and apply LOTOV | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
11 | Routine Maintenance of Electrical feeder | Chemical | Fire and explosion,dust | Burn Injury | Electrical Engineer,Electrician and contract employee | Use of dust mask and Goggle. Work instruction | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
12 | Routine Maintenance of Electrical feeder | Chemical | Fire burning of cable terminations due to over loading of feeder. | Burn Injury | Company employee | Use of dust mask and Goggle. Use of certified tools. Work instruction | 2 | 3 | 6 | Providing overload protection to the mining feeder so that in case of excess drawing of load, feeder will trip on overload so that burning of cable terminations can be avoided | HOD | In progress | 2 | 3 | 6
13 | Routine Maintenance of Electrical feeder | Chemical | Fire and explosion,dust | Burn Injury | Electrical Engineer,Electrician and contract employee | Use of dust mask and Goggle. Use of certified tools. Work instruction | 2 | 3 | 6 | Revision in work instruction WI 15, incorporating the steps taken for corrective and preventive actions. | HOD | In progress | 2 | 3 | 6
14 | Routine Maintenance of Electrical feeder | Behavioural Hazard | Hazard due Human Behaviour like non usage of PPE.Human error like non following of Work instruction. | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
15 | Routine Maintenance of Electrical feeder | Behavioural Hazard | Fire caused due to improper cooling of panels | personal injury | Electrical Engineer,Electrician and contract employee | WI/EL/15 | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
16 | Providing illumination for maintenance job | Physical | Trip / fall | personal injury | Comany Employee | Providing protective portable hand lamps with 24 volt supply duly certified by Electrical dept. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
17 | Providing illumination for maintenance job | Behavioural Hazard | Hazard due Human Behaviour like non following the SOP. Human error like usage of non certified hand lanps. | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
18 | Top charging pump motor maintenance and furnace top light maintenance | Physical | Trip / fall | personal injury | Engineer, Electrician and contract workmen | Electrical shutdown permit | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
19 | Top charging pump motor maintenance and furnace top light maintenance | Chemical | Dust and gas | Gas poisoning | Engineer, Electrician and contract workmen | PPE like dust mask,Use of gas monitor for monitoring gas level for within limit. Job to be carried out during furnace shutdown | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
20 | Top charging pump motor maintenance and furnace top light maintenance | Mechanical | Fall | personal injury | Engineer, Electrician and contract workmen | 1.Working on a safe paltform having proper hand railing. 2.Use safety belts while working at height | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
21 | Top charging pump motor maintenance and furnace top light maintenance | Behavioural Hazard | Hazard due Human Behaviour like non usage of PPE. Human error like non following of SOP. | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
22 | Hot metal crane cleaning and maintenance | Physical | 2. Contact with hot gas/metal/ slag | Burn Injury | Electrical Engineer, Electrician and contract labour | Electrical shutdown permit | 1 | 4 | 4 | Existing control measure is adequate | NA | COMPLETED | 1 | 4 | 4
23 | Hot metal crane cleaning and maintenance | Chemical | Dust and smoke | gas poisoining | Electrical Engineer, Electrician and contract labour | PPE like nose mask,ear plug,safety goggles and Canvas hand gloves with leather palm | 2 | 1 | 2 | Existing control measure is adequate | NA | COMPLETED | 2 | 1 | 2
24 | Hot metal crane cleaning and maintenance | Mechanical | Falling | personal injury | Electrical Engineer, Electrician and contract labour | Training and work instructions | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
25 | Hot metal crane cleaning and maintenance | Mechanical | Impact | personal injury | Electrical Engineer, Electrician and contract labour | Work instruction , WI/EL/14 | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
26 | Hot metal crane cleaning and maintenance | Behavioural Hazard | Hazard due Human Behaviour like non usage of PPE. Human error like not follwing the work permit procedure. | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
27 | Hot metal crane cleaning and maintenance | Physical | exposure to CO | gas poisoning | Engineer,Electrician, contractor workmen | WorkInstruction WI/EL/14,Training, Monitoring CO level while working on crane during furnace running. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
28 | Hot metal crane cleaning and maintenance | Chemical | Smoke | gas poisoning | Electrician ,Fitter and contract labour | PPE like safety as per IS 3521 goggles and nose mask as per IS 9473 . | 1 | 2 | 2 | Existing control measure is adequate | NA | COMPLETED | 1 | 2 | 2
29 | Panel work like drilling,Grinding and cutting | Ergonomics | Improper designed tools | personal injury | Electrician ,Fitter and contract labour | Work instructions for safe working, Training on Drill machine operation | 1 | 1 | 1 | Existing control measure is adequate | NA | COMPLETED | 1 | 1 | 1
30 | Panel work like drilling,Grinding and cutting | Behavioural Hazard | Hazard due Human Behaviour like non usage of Googles, Nose Mask. Human error Like slipping of drilling machine, cutting of drill bits | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
31 | Lead acid battery maintenance | Chemical | Fire and explosion.toxic chemicals,fumes | gas poisoining/ unconsiousness | Electrical Engineer, Electrician and contract labour | PPE like acid & alkaline proof hand gloves,Gas mask as per IS 9473,safety goggles, Work instructions and training | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
32 | Lead acid battery maintenance | Ergonomics | Improperly design tools | personal injury | Electrical Engineer, Electrician and contract labour | Insulated spanners, Work instructions and training | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
33 | Lead acid battery maintenance | Behavioural Hazard | Strain while handling battery | personal injury | Electrician and contract workmen | Use of handling tools like trolley for battery shifting. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
34 | Lead acid battery maintenance | Chemical | Fire and explosion if blower starts by itself when dampers are in open condition. | Burn Injury | Electrical Engineer, Electrician and contract labour | PPE like acid & alkaline proof hand gloves,Gas mask as per IS 9473,safety goggles, Work instructions and training | 2 | 3 | 6 | Modification for battery charger so that during load test of TG battery bank pure DC will be available to Blower panel. Accordingly revision in work instructions( WI 18). | HOD | In progress | 2 | 3 | 6
35 | Cable laying at height | Mechnical | Impact and falling | personal injury | Contractor employees | Using PPE like safety belts as per IS 3521 | 1 | 4 | 4 | Existing control measure is adequate |  | COMPLETED | 1 | 4 | 4
36 | Cable laying at height | Chemical | Fire | Burn Injury | Contractor employee, electrician, electrical engineer | Work instructions and training | 2 | 3 | 6 | Potect the cable from fire by proper house keeping ,Periodic cleaning of grass and other waste material so that fire hazard to the cable is not there | hOD | In progress | 2 | 3 | 6
37 | Cable laying at height | Chemical Fire | Fire | Burn Injury | Contractor employee, electrician, electrical engineer | Periodic cleaning of grass | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
38 | Cable laying at height | Chemical Fire | Fire | Burn Injury | Contractor employee |  | 2 | 3 | 6 | WI EL 22 revision incorporating the changes for proper load distibution. | HOD | In progress | 2 | 3 | 6
39 | Cable laying at height | Chemical Fire | Fire | Burn Injury | Contractor employee | WI EL 22 for proper load distibution. | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
40 | Cable laying at height | Behavioural Hazard | Hazard due Human Behaviour like non usage of PPE like safety belt | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
41 | Cable laying at height | Behavioural Hazard | Human Error Like not following of procedure, Usage of damaged safety belt | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
42 | Light repairing and changing | Physical | Electrical shock | Burn Injury | Elect. Engineer, technician and Contractor employee | Electrical shutdown permit. Work instruction and training of employee | 1 | 3 | 3 | Existing control measure is adequate | NA | COMPLETED | 1 | 3 | 3
43 | Light repairing and changing | Mechanical | Falling | personal injury | Technician and contractor emplyee | Safety belts.Work instruction and training | 1 | 3 | 3 | Existing control measure is adequate | NA | COMPLETED | 1 | 3 | 3
44 | Light repairing and changing | Mechanical | Falling | personal injury | Technician and contractor emplyee | Safety belts.Work instruction and training | 1 | 4 | 4 |  Procurement and using cage type ladders while doing lighting maint at height. | NA | In progress | 1 | 4 | 4
45 | Light repairing and changing | Mechnical | Falling of tube light fitting | personal injury | All employees sitting below the light fitting | Safety belts.Work instruction and training | 2 | 3 | 6 | Revision in work instruction WI/ELECT/19 incorporating the procedure for fixing tube light on a wooden ceiling | HOD | In progress | 2 | 3 | 6
46 | Light repairing and changing | Physical | fall of light fitting | personal injury | All employees sitting below the light fitting | WI/ELECT/19 REV 2 | 1 | 3 | 3 | Nil | NA | COMPLETED | 1 | 3 | 3
47 | Light repairing and changing | Behavioural Hazard | Hazard due Human Behaviour like following short cut, not following WI. | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
48 | Light repairing and changing | Behavioural Hazard | Human error like using damaged PPE | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
49 | Light repairing and changing | Mechnical | Falling of tube light fitting | personal injury | All employees sitting below the light fitting | WI/ELECT/19 REV 3 | 1 | 3 | 3 | Revision in work instruction WI/ELECT/19 incorporating the procedure for fixing tube light fittings with metallic/plastic reflector. | NA | In progress | 1 | 3 | 3
50 | Light repairing and changing | Mechanical . | Falling of dome type light reflector from crane top | personal injury | All employees working in the crane bay. | WI/elect/19 REV3 | 1 | 2 | 2 | Revision in work instruction WI/ELECT/19 incorporating non usage of dome type light on the crane structure. | NA | In progress | 1 | 2 | 2
51 | Light repairing and changing | Electrical | Electric shock | Burn Injury | Elect. Engineer, technician and Contractor employee | WI/elect/19 REV3 | 2 | 2 | 4 | Revision in work instruction WI/ELECT/19 incorporating procedure for disconnection of light fitting. | NA | In progress | 2 | 2 | 4
52 | Light repairing and changing | Electrical | Electric shock | Burn Injury | Elect. Engineer, technician and Contractor employee | WI/elect/19 REV4 | 1 | 3 | 3 |  | NA | Pendning | 1 | 3 | 3
53 | Welding machines maintenance | Electrical | Electric shock | Burn Injury | Electrician | Work instructions and Training., Disconnection of welding machine from supply socket | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
54 | Welding machines maintenance | Behavioural Hazard | Hazard due Human Behaviour like not disconnecting the welding machine from socket. Human error like non following of work instruction. | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
55 | Cat and Intac alternator maintenance and cleaning | Physical | Electrical | Burn Injury | Electrician | Electrical shutdown permit | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
56 | Cat and Intac alternator maintenance and cleaning | Chemical | dust | gas poisoning | Electrician | PPE like nose mask | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
57 | Cat and Intac alternator maintenance and cleaning | Behavioural Hazard | Hazard due Human Behaviour like non usage of PPE. | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
58 | Cat and Intac alternator maintenance and cleaning | Behavioural Hazard | Human error like non following of S/D procedure | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
59 | Motor and alternator greasing | Physical | Noise | personal injury | Engineer,Electrician ,fitter and contract labour | Work instructions and Training. PPE like using ear plug | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
60 | Motor and alternator greasing | Mechanical | Trapping | personal injury | Electrician ,fitter and contract labour | Work instructions and Training. | 1 | 2 | 2 | Existing control measure is adequate | NA | COMPLETED | 1 | 2 | 2
61 | Motor and alternator greasing | Behavioural Hazard | Hazard due Human Behaviour like touching the rotating part. | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
62 | Motor and alternator greasing | Behavioural Hazard | Human error Like wearing loose cloth. | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
63 | Manual shifting of material at ground level | Mechanical | fall | personal injury | Electrician ,fitter and contract labour | Work instructions and Training. | 1 | 2 | 2 | Existing control measure is adequate, | NA | COMPLETED | 1 | 2 | 2
64 | Manual shifting of material at ground level | Behavioural Hazard | Hazard due Human Behaviour like not balancing the load, Improper loading of trolley | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
65 | Manual shifting of material at ground level | Behavioural Hazard | Human error like putting hand under the material to be shifted, | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
66 | Manual shifting of material at ground level | Behavioural Hazard | Strain while handling equipment | personal injury | Electrician, Fitter and contract workmen | Use of handling tools and tackles like motor lifting rod, trolley. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
67 | Lighting DB replacement and maintenance. | Physical | Electrical | Burn Injury | Engineer,electricianand contractor employees | Work instructions | 2 | 2 | 4 | Providing ELCB proytections for all the lighting DB's | NA | COMPLETED | 2 | 2 | 4
68 | Lighting DB replacement and maintenance. | Ergonomics | Improper design tools | personal injury | Electrician and contract employee | Work instructions | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
69 | Lighting DB replacement and maintenance. | Physical | Electrical | Burn Injury | Engineer,Company workmen and contractor employees | Work instructions | 2 | 3 | 6 | For all out door installtion of LDB, providing Double door type of Lighting DB to avoid moisture on the MCB during rain. | HOD | In progress | 2 | 3 | 6
70 | Lighting DB replacement and maintenance. | Behavioural Hazard | Hazard due Human Behaviour like working on live Db without taking S/D. | personal injury/ electrocution | Engineer,Company workmen and contractor employees | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
71 | Lighting DB replacement and maintenance. | Behavioural Hazard | Human error like using damaged tools | personal injury | Engineer,Company workmen and contractor employees | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
72 | Operations of canteen electrical appliances | Physical | Electrical shock | electrocution/burn injuries | Canteen workmen | ELCB is provided for all the canteen appliances for leakage protection and checking of the same for functioning during monthly maintenance During monthlymaintenance ensure proper earthing to the equipment | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
73 | Operations of canteen electrical appliances | Behavioural Hazard | Hazard due Human Behaviour/Human error | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
74 | Replacement of cable trays | Mechanical | fall | personal injury | Electrician ,fitter and contract labour | [1]Work instructions and Training. [2]Effective supervision by the Engineer In charge | 1 | 2 | 2 | Existing control measure is adequate,Review will be done annually / base on the results | NA | COMPLETED | 1 | 2 | 2
75 | Replacement of cable trays | Behavioural Hazard | Hazard due Human Behaviour like non usage of Safety belt. | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
76 | Replacement of cable trays | Behavioural Hazard | Human error like non following of WI. | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
77 | Hot metal crane brake replacement and general maintenance | Behavioural Hazard | 1.Fingure crush injury while taking brake trial/ drive trial( 05/09/2009) | personal injury | Electrician ,fitter and contract labour | [1] Work instructions and Training. EL 14 [2] Effective supervision by the Engineer In charge | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
78 | Hot metal crane brake replacement and general maintenance | Physical | 2. Fall of object / person working from height | personal injury | Electrician ,fitter and contract labour | [1] Work instructions and Training. EL 14 [2] Effective supervision by the Engineer In charge | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
79 | Hot metal crane brake replacement and general maintenance | Behavioural Hazard | 3. Hit of pantograph to person while taking LT /CT trials | personal injury | Electrician ,fitter and contract labour | [1] Work instructions and Training. EL 14 [2] Effective supervision by the Engineer In charge | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
80 | Hot metal crane brake replacement and general maintenance | Behavioural Hazard | 4. Entanglement with moving parts while taking trial | personal injury | Electrician ,fitter and contract labour | [1] Work instructions and Training. EL 14 [2] Effective supervision by the Engineer In charge | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
81 | Hot metal crane brake replacement and general maintenance | Behavioural Hazard | 1.Not following of work instruction | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour/ | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
82 | Hot metal crane brake replacement and general maintenance | Behavioural Hazard | 2.Improper training to workmen | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour/ | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
83 | Hot metal crane brake replacement and general maintenance | Electrical | Electrical shock | electrocution/burn injuries | Electrician | Issue Shutdown permit of crane Only Electrician can work on Electrical panel/connections | 2 | 2 | 4 | Existing control measure is adequate | NA | COMPLETED | 2 | 2 | 4
84 | Hot metal crane brake replacement and general maintenance | Chemical hazard | 1.Inhalation of graphite particals | gas poisoning | Electrician ,fitter and contract labour | Use of dust mask Cleaning of graphite using vacuum cleaner | 2 | 1 | 2 | Existing control measure is adequate | NA | COMPLETED | 2 | 1 | 2
85 | Maintenance of strirrer assembly | Behavioural Hazard | Physical lime power entering into eye,getting clothes ectangled to the running stirrer shaft | personal injury | Electrician ,fitter and contract labour | Use fo PPE like safety goggles,nose mask,ear plugs and shutdown permit. Ensuring motor safety cover is put back after the job is completed and inno case stirrers are running without motor safety covers | 1 | 2 | 2 | Existing control measure is adequate | NA | COMPLETED | 1 | 2 | 2
86 | Maintenance of strirrer assembly | Behavioural Hazard | Hazard due Human Behaviour like touching the Extended rotating part | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
87 | Maintenance of strirrer assembly | Behavioural Hazard | Human error Like wearing Loose Cloth | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
88 | Issuing and normalising of electrical shutdown | Safety hazard | Phyisical –Electrical shock | personal injury | Electrician ,fitter and contract labour | Issuing and clearing of shutdown strictly as per the procedure stated in the safety manual | 1 | 3 | 3 | Existing control measure is adequate,Review will be done every six monbth/ base on the results | NA | COMPLETED | 1 | 3 | 3
89 | Issuing and normalising of electrical shutdown | Mechanical | Mechnical –Impact | personal injury | Electrician ,fitter and contract labour | Issuing and clearing of shutdown strictly as per the procedure stated in the safety manual | 2 | 2 | 4 | SP 44 procedure will be modified.incorporating the procedure for numbering new equipments in the plant | NA | In progress | 2 | 2 | 4
90 | Issuing and normalising of electrical shutdown | Behavioural hazard | Hazard due Human Behaviour/Human error like clearing of wrong S/D, Issueing of wrong S/D | personal injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
91 | Issuing and normalising of electrical shutdown | Safety hazard | Hazard due issue of shudown on a wromg feeder ( incident dated(20.10.09) | personal injury | Person who have taken shudown and his asociated workmen on the job | Shutdown permit system | 1 | 3 | 3 | Revision in Electricla shudown procedure system to in coroprate temporary clearing of shutdown. | NA | COMPLETED | 1 | 3 | 3
92 | Issuing and normalising of electrical shutdown | Safety hazard | Electrical: Hazard due to clearing of s/d without normalising at site. | personal injury | Person working on the equipment | Shutdown permit system | 2 | 3 | 6 | Revision in Eectrical S/D procedure incorporating procedure of handing over the s/d copy to the workmen working on the equipment. | HOD | COMPLETED | 2 | 3 | 6
93 | Issuing and normalising of electrical shutdown | Safety hazard | Electrical: Hazard due to clearing of s/d without normalising at site. | personal injury | Person working on the equipment | Shutdown permit system Reviewed after Incident dated 12.04.2011. | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
94 | Issuing and normalising of electrical shutdown | Safety hazard | Electrical:Hazard due putting the fuse in the panel without s/d being cleared | personal injury | Person working on the equipment | Shutdown permit system | 2 | 3 | 6 | Revision in Eectrical S/D procedure incorporating procedure to be followed in case of non availibilty of LOTO. | HOD | COMPLETED | 2 | 3 | 6
95 | Restoring of power supply from power plant after total power failure | Chemical hazard | Chemical hazard Gas | Poisoning, unconsciousness | Production staff | Work instruction WI/PP/03 . Training of employees on the said work instruction | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
96 | Restoring of power supply from power plant after total power failure | Behavioural hazard | Hazard due Human Behaviour/Human error like Switching ON/OFF of wrong feeder, Mis synchronising | personal injury | Production staff & workmen | Training of employees, Provision of sufficient interlocks. Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
97 | Restoring of power supply from power plant after total power failure | Physical | Physical Electrical | personal injury | Electrician | Isolation of Electric supply before starting the job | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
98 | Restoring of power supply from power plant after total power failure | Mechanical | Mechanocal Falling | personal injury | Electrician | Use of certfied ladders to work on height | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
99 | Restoring of power supply from power plant after total power failure | Mechanical | Mechanocal Impact | personal injury | All Employees | Use of standard nut bolts for fan fixing, Yearly Checking of ceiling fan installation on safety angle,Cross checking of new installations by Engineer incharge | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
100 | Restoring of power supply from power plant after total power failure | Mechanical | Mechanical Fall of exahust fan | personal injury | Employees working in area where exahust fan is fitted | Awareness , training | 1 | 3 | 3 | 1.Checking of all exahust fan for proper mounting. 2.Installation of locking chain for exahust fan which will hold the fan in case of fall of fan. 3. Fans will be fitted with the protection guard | NA | In progress | 1 | 3 | 3
101 | Restoring of power supply from power plant after total power failure | Behavioural hazard | Hazard due Human Behaviour/Human error Like use of non certified ladders, Non isolation of Electrical supply. | personal injury | Employees working in the area where the fan is fitted | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
102 | Restoring of power supply from power plant after total power failure | Mechanincal | Mechanical Fall of Ceiling fan due to cutting or bolt. | personal injury | Employees in that area | Use of standard nut bolts for fan fixing, Yearly Checking of ceiling fan installation on safety angle,Cross checking of new installations by Engineer incharge | 2 | 2 | 4 | Refer Objective EPI 05/2012 | NA | COMPLETED | 2 | 2 | 4
103 | Loading, shfting and installation of electrical panel | Mechanical | Mechanical Falling and impact | personal injury | Engineer, Electrician and contract workmen | Check for panel lifting hooks for proper fittings,Use proper slings and tested chain pulley block for lifting panels, effective supervision whlie lifting unloading and installation. | 2 | 2 | 4 | Nil | NA | COMPLETED | 2 | 2 | 4
104 | Loading, shfting and installation of electrical panel | Behavioural hazard | Hazard due Human Behaviour/Human error Like putting hand/finger under the panel, Standing very close to panel while being shifted, usage of damaged slings | personal injury | Engineer, Electrician and contract workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
105 | Loading, shfting and installation of electrical panel | Physical | Strain while handling equipment | personal injury | Electrician, Fitter and contract workmen | Use of handling tools like hydra for panel unloading, trolley/ crane mounted truck for panel shifting. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
106 | Meggering of Electrical equipments and earth resistance measurement | Physical | Physical Electrical | personal injury | Engineer, Electrician and contract workmen | *Ensure that the meggering leads are properly insulated .*Ensure that the equipment/s under test is made electrically dead. * Ensure that the equipment under test and megger terminals are discharged to the earth by using insulated shorting lead. | 1 | 2 | 2 | Nil | NA | COMPLETED | 1 | 2 | 2
107 | Meggering of Electrical equipments and earth resistance measurement | Electrical | Electrical shock (14/07/060) | personal injury | Engineer, Electrician and contract workmen | *Ensure that the equipment/s under test is made electrically isolated. Reviewed after implementing control measure | 2 | 3 | 6 | 1.Training of employee on activity work intructions. 2.Display of Danger notice" Isolate before opneing" on the HT feeder out going. | HOD | Pending | 2 | 3 | 6
108 | Meggering of Electrical equipments and earth resistance measurement | Electrical | Electrical shock | personal injury | Engineer, Electrician and contract workmen | *Ensure that the meggering leads are properly insulated .*Ensure that the equipment/s under test is made electrically dead. * Ensure that the equipment under test and megger terminals are discharged to the earth by using insulated shorting lead. | 1 | 2 | 2 | Nil | NA | COMPLETED | 1 | 2 | 2
109 | Meggering of Electrical equipments and earth resistance measurement | Behavioural hazard | Hazard due Human Behaviour/Human error Like not discharging after doing meggering, Touching the panel while meggering | personal injury | Engineer, Electrician and contract workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
110 | Transformer installation, testing,commissioning and general maintenance. | Electrical | Physical (Electrical) | personal injury | Electrician and contractor emplyeee | work instruction WI/ELECT/16 | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
111 | Transformer installation, testing,commissioning and general maintenance. | Mechanical | Mechanical (falling) | personal injury | Electrician and contractor emplyeee | Training of emplyee | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
112 | Transformer installation, testing,commissioning and general maintenance. | Behavioural hazard | /Human error Like Usage of inedequate capacity loading vehicle, | personal injury | Electrician and contractor emplyeee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
113 | Transformer installation, testing,commissioning and general maintenance. | Behavioural hazard | Hazard due Human Behaviour like Opening of transformer terminal box without taking S/D | personal injury | Electrician and contractor emplyeee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
114 | Shifting of ladder and working on height using ladder. | Mechanical | Mechanical Fall from height | personal injury | Electrician and contractor employee | work instruction SP 44 Working at height using ladder | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
115 | Shifting of ladder and working on height using ladder. | Electrical | Electrical Electrical shock with overhead line while shifting ladder (28/07/06) | personal injury | Electrician and contractor employee | Electrician can work on Electrical panel/connections | 1 | 4 | 4 | 1.Shifting of ladder horizontally . 2.Training of concerned people on shifting ladder. 3. Revisions in WI incorporating the procedure for shifting ladder | NA | Pending | 1 | 4 | 4
116 | Shifting of ladder and working on height using ladder. | Electrical | Electrical Electrical shock with overhead line while shifting ladder (28/07/06) | personal injury | Electrician and contractor employee | WI/ELECT/21 | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
117 | Shifting of ladder and working on height using ladder. | Behavioural hazard | Hazard due Human Behaviour like bending & working on the ladder | personal injury | Electrical Engineer, Electrician and contractor employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
118 | Shifting of ladder and working on height using ladder. | Behavioural hazard | Human error Like not placing the order properly | personal injury | Electrical Engineer, Electrician and contractor employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
119 | Maintenance of water cooler and deep fridge | Electrical | Electrical Shock | personal injury | Electrician and contract employee | WI/ELECT/15 | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
120 | Maintenance of water cooler and deep fridge | fire hazard | Fire:Capacitor bursting and catching fire | personal injury | Electrician and contract employee | 1.Checking the healthiness of capacitor during monthly maintenenec and replacing the same if it has deteriorated | 1 | 1 | 1 | Existing control measures are adequate | NA | COMPLETED | 1 | 1 | 1
121 | Maintenance of water cooler and deep fridge | Behavioural hazard | Hazard due Human Behaviour like like not disconnecting the power supply before working. | personal injury | Electrician and contract employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
122 | Maintenance of water cooler and deep fridge | Physical | Human error like not following the work permit | personal injury | Electrician and contract employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
123 | Attending plant breakdowns. | Electrical | Electrical Shock | personal injury | Electrician and contract employe | WI/EL/15 and WI/EL/16 | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
124 | Attending plant breakdowns. | Mechanical | Mechanical Fall , getting trapped , burn injuries, | personal injury | Electrician and contract employee | SP 44 | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
125 | Attending plant breakdowns. | Chemical hazard | Chemical Fire and explosion | personal injury equipment damage | Electrician and contract employee | Guidelines to attend the plant breakdowns. | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
126 | Attending plant breakdowns. | Behavioural hazard | Hazard due Human Behaviour/Human error like attending breakdowns at night without Torch, Running to attend the breakdown | personal injury | Electrician and contract employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
127 | Attending plant breakdowns. | Mechanical hazard | Mechanical Fall | personal injury | Engineer,Electrician and contract employee | SP 44 | 2 | 3 | 6 | Modification in WI 10 | HOD | COMPLETED | 2 | 3 | 6
128 | Attending plant breakdowns. | Mechanical hazard | Mechanical Fall | personal injury | Engineer,Electrician and contract employee | SP 44 | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
129 | Attending plant breakdowns. | Electrical hazard | Electric shock by touching part of the body to the switches mounted on the panel door | personal injury | Electrician and contract employee | WI/EL/15 and WI/EL/16 | 2 | 2 | 4 | Insulating all the door mounted switches by providing backelite & by applying insulating spray | NA | COMPLETED | 2 | 2 | 4
130 | Attending plant breakdowns. | electrical hazard | Electric shock by touching part of the body to the switches mounted on the panel door | personal injury | Electrician and contract employee | WI/EL/15 and WI/EL/16 | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
131 | Attending plant breakdowns. | Physical hazard | Physical fall hazard due to sliiping on the coir mat placed infront of the panel room/Office door | personal injury | Engineer,Electrician and contract employee | Guidelines to attend the plant breakdowns. | 2 | 2 | 4 | Removal of all such coir mats from offices & panel rooms. |  | Pending | 2 | 2 | 4
132 | Attending plant breakdowns. | Physical hazard | Physical fall hazard due to sliiping on the coir mat placed infront of the panel room/Office door | personal injury | Engineer,Electrician and contract employee | Guidelines to attend the plant breakdowns. | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
133 | Attending plant breakdowns. | Physical hazard | Phisical Hazard like any body part getting trapped in the equipment due to automatic operation of equipment. | personal injury | Engineer, Workmen and contract employee | Guidelines to attend the plant breakdowns. | 2 | 3 | 6 | Modification in WI 10, including process of proper communication while taking trials. | HOD | COMPLETED | 2 | 3 | 6
134 | Attending plant breakdowns. | Physical hazard | Phisical Hazard like any body part getting trapped in the equipment due to automatic operation of equipment. | personal injury | Engineer, Workmen and contract employee | Guidelines to attend the plant breakdowns. | 1 | 3 | 3 | Existing control measures are edequate | NA | COMPLETED | 1 | 3 | 3
135 | 25x12T crane & 12T magnet crane cleaning & maintenance | Physical hazard | Physical Electrical shock | personal injury | Engineer, Electrician, Contract Labour | Electrical S/D, close coordination & supervision. | 1 | 3 | 3 | Existing control measures are edequate | NA | COMPLETED | 1 | 3 | 3
136 | 25x12T crane & 12T magnet crane cleaning & maintenance | Chemical hazard | Chemical : Dust ,Vapour, smoke | Poisoning, unconsciousness | Engineer, Electrician, Contract Labour | Use of PPE's like dust mask as per IS 9473, safety googles & Canvas Hand gloves | 2 | 2 | 4 | Existing control measures are edequate | NA | COMPLETED | 2 | 2 | 4
137 | 25x12T crane & 12T magnet crane cleaning & maintenance | Mechanical hazard | Mechanicl: tarpping | personal injury | Engineer, Electrician, Contract Labour | Work permit & Electrical S/D, use of safety belts while working at hieght,Training of Employee to carry out tha maintenance task. | 1 | 3 | 3 | Existing control measures are edequate | NA | COMPLETED | 1 | 3 | 3
138 | 25x12T crane & 12T magnet crane cleaning & maintenance | Behavioural hazard | Hazard due Human Behaviour/Human error Trying to cross the platform without handrailing support. | personal injury | Engineer, Electrician, Contract Labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are edequate | NA | COMPLETED | 2 | 2 | 4
139 | 25x12T crane & 12T magnet crane cleaning & maintenance | Mechanical hazard | Hazard due Hit of crane LT girder on mechnical stopper due to limit switch failure (Incident dated 25.08.09) | personal injury | Emplyees working on the crane | monthly Maintenace check list to check fucntiong of limit switch | 2 | 2 | 4 | Existing control measures are edequate | NA | COMPLETED | 2 | 2 | 4
140 | 25x12T crane & 12T magnet crane cleaning & maintenance | safety hazard | Hazard due to Brake loose & hook lowering automatically(Incident dated 10.11.11) Aftyer implementation of C & P | personal injury, equipment damage | Emplyees working on the crane | monthly Maintenace check list to check single brake operation | 4 | 2 | 8 | Effective implementation of checklist. Checking with singel brake operation | HOD | In progress | 4 | 2 | 8
141 | 25x12T crane & 12T magnet crane cleaning & maintenance | safety haard | Hazard due to Brake loose & hook lowering automatically(Incident dated 10.11.11) | personal injury, equipment damage | Emplyees working on the crane | monthly Maintenace check list to check single brake operation | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
142 | 25x12T crane & 12T magnet crane cleaning & maintenance | safety hazard | Lowering of Crane automatically, X | personal injury | Employees working in crane area | monthly Maintenace check list to check single brake operation, Reviewed after C & P | 4 | 2 | 8 | Effective implementation of checklist. Checking with singel brake operation | HOD | In progress | 4 | 2 | 8
143 | 5T grab crane cleaning & maintenance | Physical hazard | Physical Electrical Shock | personal injury | Engineer, Electrician, Contract Labour | Electrical S/D | 1 | 2 | 2 | Existing control measures are edequate | NA | COMPLETED | 1 | 2 | 2
144 | 5T grab crane cleaning & maintenance | Chemical hazard | Chemical : Dust ,Vapour | Poisoning, unconsciousness | Engineer, Electrician, Contract Labour | Use of PPE's | 2 | 2 | 4 | Person should not be on the crane when granulation is on. | NA | COMPLETED | 2 | 2 | 4
145 | 5T grab crane cleaning & maintenance | Behavioural hazard | Hazard due Human Behaviour/Human error Like trying to enter the crane while moving. | personal injury | Engineer, Electrician, Contract Labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
146 | 5T grab crane cleaning & maintenance | Mechanical hazard | Hazard due to lowering of grab bucket due to losse setting of brake(Incident: On 07.10.09) | personal injury, equipment damage | Production/ maintenance staff & workmen working in that area | Monthly maintenance of crane and weekly brake inspection | 2 | 2 | 4 | Production shall ensure that the grab bucket is kept down on the ground when the crane is not in operation | NA | COMPLETED | 2 | 2 | 4
147 | 5T grab crane cleaning & maintenance | Physical hazard | Physical Electrical Shock while working on the control switch box | personal injury | Production/ maintenance staff & workmen working in that area | Monthly maintenance of crane and weekly brake inspection | 4 | 2 | 8 | Production to Ensure that cleaning of the operating station is not done using water hose pipe & SOP to be modified accordingly. | HOD | COMPLETED | 4 | 2 | 8
148 | 5T grab crane cleaning & maintenance | physical hazard | Physical Electrical Shock while working on the control switch box | personal injury | Production/ maintenance staff & workmen working in that area | Monthly maintenance of crane and weekly brake inspection | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
149 | 5T grab crane cleaning & maintenance | electricla hazard | Operator got mild shock while touching the hook. | personal injury | Production/ maintenance staff & workmen working in that area | Monthly maintenance of crane and weekly brake inspection | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
150 | 5T grab crane cleaning & maintenance | electrical hazard | Physical Electrical Shock while working on the control switch box | personal injury | Production/ maintenance staff & workmen working in that area | Monthly maintenance of crane and weekly brake inspection | 4 | 2 | 8 | Providing direct earthing for all cranes | HOD | COMPLETED | 4 | 2 | 8
151 | 5T grab crane cleaning & maintenance | electrical hazard | Physical Electrical Shock while working on the control switch box | personal injury | Production/ maintenance staff & workmen working in that area | Monthly maintenance of crane and weekly brake inspection | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
152 | Maintenance of stove hydralic Valves & limit switches | Physical hazard | Physical Electric shock,contact with high temperature. | personal injury | Engineer, Electrician, Contract labour | Do not touch the Stove surface & Hot blast line, Electrical S/D permit | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
153 | Maintenance of stove hydralic Valves & limit switches | chemical hazard | Chemical: Inhalation of Carbon Monoxide | Poisoning, unconsciousness | Engineer, Electrician, Contract labour | Continous monitoring of CO level by using CO monitor. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
154 | Maintenance of stove hydralic Valves & limit switches | mechanical hazard | Mechanical:Fall from height, trapping | personal injury | Engineer, Electrician, Contract labour | Use of Safety belt as per IS 3521, Proper training for the person performing the task. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
155 | Maintenance of stove hydralic Valves & limit switches | Behavioural hazard | Hazard due Human Behaviour/Human error Like trying to lubricate the limit switches while valve in operation, touching the hot surface of the stove. | personal injury | Engineer, Electrician, Contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
156 | PCM Launder crane maint | Physical hazard | Physical Electrical | personal injury | Electrical Engineer, Electrician and contract labour | Electrical shutdown .permit. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
157 | PCM Launder crane maint | chemical hazard | Chemical Dust/powder, smoke | Poisoning, unconsciousness | Electrical Engineer, Electrician and contract labour | PPE like nose mask,safety goggles and Canvas hand gloves with leather palm. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
158 | PCM Launder crane maint | mechanical haard | Mechanical Traping,Falling | personal injury | Electrical Engineer, Electrician and contract labour | Use of PPE'S like safety belt as per IS 3521 | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
159 | PCM Launder crane maint | Behavioural hazard | Hazard due Human Behaviour/Human error like non usage of PPE, non following of S/D procedure. Review after Incident Dated: 25/05/2012 Wire rope got cut due to limit switch not functioning. | personal injury | Production staff & workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
160 | PCM Launder crane maint | mechanical | Mechanical Wire rope cutting & crane falling | personal injury, equipment damage | Electrical Engineer, Mechanical Engineer, Electrician, Mechanical fitter, production staff, workemen and contract labour, | Work Instruction WI/EL/10 | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
161 | Electrical maint of pantoon pumps | Physical hazard | Physical Electrical | personal injury | Electrical Engineer,Electrician and contract employee | Electrical s/d | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
162 | Electrical maint of pantoon pumps | mechanical hazard | Mechanical: Falling | personal injusry | Electrical Engineer,Electrician and contract employee | Use of safety belt as per IS 3521 while working at pantoon. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
163 | Electrical maint of pantoon pumps | Behavioural hazard | Hazard due Human Behaviour/Human error Like non usage of Safety belt | personla injury | Electrical Engineer,Electrician and contract employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
164 | Cleaning of 33 kv substation insulators and 11 kv overhead line maintenance | Electrical hazard | Physical Electrical | personla injury | Electrical Engr, Electrician and contract employee | Shutdown permit. Use of discharge rod | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
165 | Cleaning of 33 kv substation insulators and 11 kv overhead line maintenance | Mechanical hazard | Mechanical Falling | personla injury | Electrical Engr, Electrician and contract employee | Training of Employee. Work instruction. | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
166 | Cleaning of 33 kv substation insulators and 11 kv overhead line maintenance | Behavioural hazard | Hazard due Human Behaviour Like not taking S/D permit. Human error like not using discharge rod. | personla injury | Elect. Engr,Electrician, Fitter and contact workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
167 | SPM and vibration measurements | Physical hazard | Physical Noise, Vibration | Personal injury | Electrician, Contract Labour | Use of PPE's like Ear Plug | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
168 | SPM and vibration measurements | Chemical hazard | Chemical : Dust, Gas | Poisoning, unconsciousness | Electrician, Contract Labour | Use of PPE's like Nose mask as per IS 9473, Co monitor | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
169 | SPM and vibration measurements | Mechanical hazard | Mechanical: Trapping | Personal injury | Electrician, Contract Labour | Avoiding use of Loose clothes. Proper handling of meter chords while measurments. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
170 | SPM and vibration measurements | Behavioural hazard | Hazard due Human Behaviour/Human error Like touching the rotating parts | Personal injury | Production staff & workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
171 | Scrap shifting | Mechanical hazard | Mechnical: Traping, Falling of material | Personal injury | Electrician and contract employee | On the job training of employee, Use of Canvas Hand Gloves, | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
172 | Scrap shifting | Behavioural hazard | Hazard due Human Behaviour/Human error Shifting of material without usage of PPE | Personal injury | Electrician and contract employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
173 | Operation of 2.3 KVA Portable Generator set | Physical hazard | Physical noise vibration. | Personal injury | Engineer, Electrician, Contract Labour | Operating procedure provided on the generator set | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
174 | Operation of 2.3 KVA Portable Generator set | Gas hazard | Chemical Fire & Explosion, Smoke | Poisoning, unconsciousness | Engineer, Electrician, Contract Labour | Operating procedure provided on the generator set | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
175 | Operation of 2.3 KVA Portable Generator set | Behavioural hazard | Hazard due Human Behaviour/Human error like not following the SOP | Personal injury | Engineer, Electrician, Contract Labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
176 | 4T grab crane cleaning & maintenance | Behavioural Hazard | Physical lime power entering into eye,getting clothes ectangled to the running stirrer shaft | personal injury | Electrician ,fitter and contract labour | Use fo PPE like safety goggles,nose mask,ear plugs and shutdown permit. Ensuring motor safety cover is put back after the job is completed and inno case stirrers are running without motor safety covers | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
177 | 4T grab crane cleaning & maintenance | Behavioural Hazard | Hazard due Human Behaviour like touching the Extended rotating part | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 1 | 1 | 1 | Person should not be on the crane when granulation is on. | NA | COMPLETED | 1 | 1 | 1
178 | 4T grab crane cleaning & maintenance | Behavioural Hazard | Human error Like wearing Loose Cloth | personal injury | Electrician ,fitter and contract labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
179 | Maintenance of Thickner Rack & accessories | Electrical Hazard | Electrical shock | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | Electrical S/D | 2 | 2 | 4 | Existing control measures are edequate | NA | COMPLETED | 2 | 2 | 4
180 | Maintenance of Thickner Rack & accessories | Chemical Hazard | 1.Inhalation of graphite particals,Gas Leakages | Gas poisoning, Unconsiousness | Engineer,Engineer, Electrician, Contract Labour | Use of PPE's Like nose mask as per IS 9473 | 2 | 1 | 2 | Existing control measures are edequate | NA | COMPLETED | 2 | 1 | 2
181 | Maintenance of Thickner Rack & accessories | Mechanical Hazard | Mechanical: Falling | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour | Working on safe platform having proper hand railing | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
182 | Maintenance of Thickner Rack & accessories | Behavioural Hazard | Hazard due Human Behaviour/Human error like putting hand in the thickner water, putting hand in the rotating chain | personal injury, Equipment damage | Production staff & workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
183 | Electrical panel installation | Electrical Hazard | Electrical shock | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | Electrical S/D | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
184 | Electrical panel installation | Chemical Hazard | Chemical : Smoke inhaling while welding activity | Gas poisoning, Unconsiousness | Engineer,Engineer, Electrician, Contract Labour | Use of PPE's like Nose mask as per IS 9473 | 2 | 1 | 2 | Existing control measures are edequate | NA | COMPLETED | 2 | 1 | 2
185 | Electrical panel installation | Mechanical Hazard | Mechanical: Falling, impact | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour | Safe handling of panel while shifting and installtion. While shifting panel with hydra, maintain atleast 04 mts clearance for a person who is carrying and holding the panel with rope .Never allow panel to install with a door having hinges placed horizontally as it may fall down while opening for maintenece | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
186 | Electrical panel installation | Behavioural Hazard | Hazard due Human Behaviour/Human error like putting hand under the panel, unbalance loading & pushing of panel. | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
187 | Electrical panel installation | Mechanical Hazard | Hazard due to not placing/locking of chequered plate on panel trench ( Identified for the nearmiss case dated 11.09.2009 ) | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour, other dept employee while walking inside the panel room | Locking of chequered plate by welding angle only on two side for locking | 1 | 3 | 3 | Locking of chequered plate from all side by welding angle from inside so as to lock the chequered plate in its position | NA | In progress | 1 | 3 | 3
188 | Cable jointing with Raychem jointing kit | Electrical Hazard | Electrical shock | electrocution/burn injuries | Electrician and contract employee | Use Electical applinaces with ELCB protections. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
189 | Cable jointing with Raychem jointing kit | Mecanical Hazard | Mechanical Fall , getting trapped , burn injuries while using hot air gun | personal injury, Equipment damage | Electrician and contract employee | Traing of employee, | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
190 | Cable jointing with Raychem jointing kit | Behavioural Hazard | Hazard due Human Behaviour/Human error like putting finger in the blow lamp | personal injury, Equipment damage | Electrician and contract employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
191 | Erection of GEPL BFG line | Electrical Hazard | Electrical shock | electrocution/burn injuries | Contractor employee | SP 44 Procedure to work in the vicinity of High voltage overhead line | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
192 | Erection of GEPL BFG line | Mechanical Hazard | Fall of person from height | Personal injury | Electrician and contract employee | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
193 | Erection of GEPL BFG line | Mechanical Hazard | Fall of object , tools from height | personal injury, Equipment damage | Contractor employee | Traing of employee on SP 44, WI/Maint/12,94,92,15 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
194 | Erection of GEPL BFG line | Mechanical Hazard | trapping , entaglement of material while material handling | personal injury, Equipment damage | Contractor employee | Traing of employee on SP 44, WI/Maint/12,94,92,16 | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
195 | Erection of GEPL BFG line | Mechanical Hazard | Failure of slings, chain pulley bock, etc | personal injury, Equipment damage | Contractor employee | Traing of employee on SP 44, WI/Maint/12,94,92,17 | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
196 | Erection of GEPL BFG line | Chemical Hazard | gas poisoning | Gas poisoning, Unconsiousness | Electrician and contract employee | training on WI/maint/22 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
197 | Erection of GEPL BFG line | Behavioural Hazard | Hazard due Human Behaviour/Human error like not taking 11 KV O/h line S/D | Personal injury | Production staff & workmen | Training of employees,Surprise checks on employees behaviour while working. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
198 | Transformer oil testing | Electrical Hazard | Electrical shock | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | Proper Earthing for the oiltesting machine. Limit switch interlock for door of high voltage compartment, on the job training totechnician | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
199 | Transformer oil testing | Behavioural Hazard | Hazard due Human Behaviour/Human error like putting hand under the panel, unbalance loading & pushing of panel. | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour | Training of employees,Surprise checks on employees behaviour while working. | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
200 | Transformer oil testing | Chemical Hazard | Physical Splashing of Hot Transformer oil with high pressure | personal injury | Elect. Engr,Electrician, Oil filteration Kit Operator | No loose connections to be left while connecting the hoses. | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
201 | Underground cable laying | Mechanical Hazard | Mechnical – Person falling in trench | personal injury | All Employees concerned working in the area. | Work permit, area barrication. Work instructions and training | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
202 | Underground cable laying | Behavioural Hazard | Hazard due Human Behaviour/Human error like not following of WI | personal injury | Production staff & workmen | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
203 | Underground cable laying | Chemical : | Dust , | Soffocation, personal injury | Engineer, Electrician, Contract Labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
204 | Underground cable laying | Electrical Hazard | short circuit of cable due to mechanical damage and water entry. | personal injury, Equipment damage | Engineer, Electrician, Contract Labour | Work instruction no 22 Rev 6( Cable laying and tray erection). | 2 | 3 | 6 | Revision in work instruction no 22 Rev 6( Cable laying and tray erection). | HOD | COMPLETED | 2 | 3 | 6
205 | Light Fixture installation | Electrical Hazard | Electrical shock | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | Electrical S/D | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
206 | Light Fixture installation | Chemical Hazard | gas poisoning | Gas poisoning, Unconsiousness | Electrician and contract employee | Use of PPE's like nose mask as per IS 9473 | 2 | 1 | 2 | Existing control measures are edequate | NA | COMPLETED | 2 | 1 | 2
207 | Light Fixture installation | Mechanical haxard | Mechanical: Falling, impact | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour | Use of Certified ladder | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
208 | Light Fixture installation | Behavioural Hazard | Hazard due Human Behaviour/Human error | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
209 | Light Fixture installation | Mechanical hazard | Fall of light fitting | personal injury, Equipment damage | Plant emplyee, contractor employee | WI/ELECT/19 | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
210 | Light Fixture installation | Mechanical Hazard | Fall of hanging type light fitting from Crane bay(Identified from incident dated 19.03.10) | personal injury, Equipment damage | All employess working in the area | Non installation of Hanging type light fitting on the moving crane | 1 | 1 | 1 | No hanging type fittings will be installed on the moving crane in future. | NA | In progress | 1 | 1 | 1
211 | HBS hoist maintenance | Electrical Hazard | Electrical shock | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | Electrical S/D | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
212 | HBS hoist maintenance | Chemical Hazard | gas poisoning | Gas poisoning, Unconsiousness | Engineer,Engineer, Electrician, Contract Labour | Use of PPE's Like Nose mask as per IS 9473, use of CO monitor. | 1 | 4 | 4 | Existing control measures are edequate | NA | COMPLETED | 1 | 4 | 4
213 | HBS hoist maintenance | Mechanical haxard | Mechanical: Falling, impact | personal injury, Equipment damage | Engineer, Electrician, Contract Labour | Use of safety belt as per IS 3521 | 1 | 3 | 3 | Existing control measures are edequate | NA | COMPLETED | 1 | 3 | 3
214 | HBS hoist maintenance | Behavioural Hazard | Hazard due Human Behaviour/Human error Like non usage of PPE. | Personal injury | Engineer, Electrician, Contract Labour | Training of employees,Surprise checks on employees behaviour while working. | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
215 | HBS hoist maintenance | External / Natural Hazard | Presence of honey comb | Personal injury | Engineer, Electrician, Contract Labour | Beware of Honey bees Board installed at the entrance of the gate | 2 | 2 | 4 | Operate crane from lower platform to ensure that there is no presence of honey comb along the crane platform and crane pantograph. | NA | In progress | 2 | 2 | 4
216 | Overhead line pole maintenance | Mechanical haxard | Mechanical: Falling, impact | personal injury, Equipment damage | All Employees concerned working in the area. | Work permit, area barrication. Task to be carried out only by skilled person, Use of HIAB, Use of safety belt as per IS 3521 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
217 | Overhead line pole maintenance | Electrical Hazard | Electrical shock | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | Electrical S/D permit,WI/ELECT/16 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
218 | Overhead line pole maintenance | Behavioural Hazard | Hazard due Human Behaviour/Human error Like trying to climp on the pole without using Hiab, Standing with unbalance on the Hiab. | Personal injury | Production staff & workmen | Training of employees,Surprise checks on employees behaviour while working. | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
219 | Unbalance motor replacement | Mechanical haxard | Mechnical – Fall of motor | personal injury, Equipment damage | All Employees concerned working in the area. | Work permit, WI/ELECT/25 | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
220 | Unbalance motor replacement | Electric shock | Electric shock | personal injury, Equipment damage | Person carrying out the task | Electrical S/D permit,WI/ELECT/25 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
221 | Unbalance motor replacement | Behavioural Hazard | Hazard due Human Behaviour/Human error like tigtening the bolts without torque wrench | personal injury, Equipment damage | Production staff & workmen | Training of employees,Surprise checks on employees behaviour while working. | 1 | 1 | 1 | Existing control measures are adequate | NA | COMPLETED | 1 | 1 | 1
222 | Motor trial | Mechanical hazard | Mechnical – Fall of motor | personal injury, Equipment damage | All Employees concerned working in the area. | WI/El/06,SP 44 H | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
223 | Motor trial | Electrical Hazard | Electric shock | personal injury, Equipment damage | Person carrying out the task of Electrical connections. | WI/EL/06,WI/EL/11, Shutdown of feeder while giving motor connection. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
224 | Motor trial | Mechanical Hazard | Hit due to flying object of rotating motor . | personal injury, Equipment damage | All Employees concerned working in the area. | WI/El/06,Ensure half coupling, shaft key is removed while taking trial. No unauthorised entry | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
225 | Motor trial | Mechanical Hazard | Entanglement with rotating parts of motor under trial | personal injury, Equipment damage | All Employees concerned working in the area. | Ensure safety cage having sinage board " motor under trial has to be placed on motor. No unauthorised entry | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
226 | Motor trial | Behavioural Hazard | Hazard due Human Behaviour/Human error Like taking trial with Shaft key, Touching the rrotating part, not barricading the area. | personal injury, Equipment damage | All Employees concerned working in the area. | Training of employees,Surprise checks on employees behaviour while working. | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
227 | Annual preventive maintenance of panel | Mechanical Hazard | Fall of person from panel top | personal injury, Equipment damage | Engineer,Electrician and contractor employees | SP 44 working at height | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
228 | Annual preventive maintenance of panel | Electrical Hazard | Electric shock/Electric shock due to back feeding from temporary supply leakage | personal injury, Equipment damage | Engineer,Electrician and contractor employees | WI/EL/15,WI/EL/16 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
229 | Annual preventive maintenance of panel | Chemical Hazard | Inhaling of dust while cleaning panel | personal injury, Equipment damage | Engineer,Electrician and contractor employees | use of Nose mask as per IS 9473 | 2 | 1 | 2 | Existing control measures are adequate | NA | COMPLETED | 2 | 1 | 2
230 | Annual preventive maintenance of panel | Behavioural Hazard | Human Behavior of not following work instructions, not using PPE | personal injury, Equipment damage | Engineer,Electrician and contractor employees | Training of employees,Surprise checks on employees behaviour while working. | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
231 | Highmast lighting tower Hoisting/Lowering,Maint cable/wire rope replacement | Electrical Hazard | Electrical shock | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | WI/EL/19 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
232 | Highmast lighting tower Hoisting/Lowering,Maint cable/wire rope replacement | Safety Hazard | Crush injury while lowering high mast cradle. | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour | Be away from the high mast tower area while lowering electrically. Safety Awareness/traning Use of PPE like hand gloves | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
233 | Highmast lighting tower Hoisting/Lowering,Maint cable/wire rope replacement | Mechanical hazard | Fall of material while handling HMT | personal injury, Equipment damage | Engineer,Engineer, Electrician, Contract Labour | Be away from the high mast tower area while hndling high mast tower Safety Awareness/traning Use of PPE like helmet gloves | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
234 | Highmast lighting tower Hoisting/Lowering,Maint cable/wire rope replacement | Electrical Hazard | Contact ( Electrocution)with overhead live line while handling high mast tower by crane | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | Ensure that the surrounding overhead lines are made dead while handling high mast tower lifting / shifting activity. Safety Awareness/traning, Use of PPE | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
235 | Highmast lighting tower Hoisting/Lowering,Maint cable/wire rope replacement | Behavioural Hazard | Hazard due Human Behaviour/Human error like non usage of PPE | Personal injury | Contract person | Briefing of contractor person | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
236 | Highmast lighting tower Hoisting/Lowering,Maint cable/wire rope replacement | Mechanical hazard | Toppling of crane | personal injury, Equipment damage | Crane operator , workmen standing surrounding area | Place crane on a levelled surface. Ensure operator is trained to operate crane. Do not lift load more than the crane lifting limit. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
237 | Highmast lighting tower Hoisting/Lowering,Maint cable/wire rope replacement | Safety Hazard | Entanglement with moving wire rope while adjusting rope over pulley. | Personal injury | Workmen handling the task | Training of workmen for awareness on ectanglement from rotating parts. | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
238 | Welding outlet maintenance | Electrical Hazard | Electrical shock | electrocution/burn injuries | Engineer,Engineer, Electrician, Contract Labour | WI/EL/19 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
239 | Welding outlet maintenance | Chemical Hazard | Presence of CO | Gas poisoning, Unconsiousness | All Employees concerned working in the area. | Co level to be monitored continously, Person carrying out the job has to carry portable oygen cylinder. Person should be trained to use oxygen cylinder. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
240 | Welding outlet maintenance | Behavioural Hazard | Human behavior like not closing the outlet properly | personal injury, Equipment damage | All Employees concerned working in the area. | WI | 1 | 2 | 2 | Existing control measures are adequate | NA | COMPLETED | 1 | 2 | 2
241 | Lightening arrestor installation | Safety Hazard | Fall of LA, Fall of person from height. | Personal injury | All Employees concerned working in the area. | SP 44, Inspection of LA for proper installation | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
242 | Lightening arrestor installation | Chemical Hazsard | Dust | Gas poisoning, Unconsiousness | All Employees concerned working in the area. | use of PPE like nose mask as per IS 9473 | 1 | 1 | 1 | Existing control measures are adequate | NA | COMPLETED | 1 | 1 | 1
243 | Lightening arrestor installation | Chemical Hazsard | CO Gas | Gas poisoning, Unconsiousness | Person working in that area | CO level to be monitored continously. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
244 | Lightening arrestor installation | Behavioural Hazard | Hazard due Human Behaviour/Human error like not installing the LA with proper support | personal injury, Equipment damage | All Employees concerned working in that area. | Training of employees,Surprise checks on employees behaviour while working. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
245 | Removal of old ,unwanted cables | Electrical Hazard | Electrical shock | electrocution/burn injuries | Electrician | WI/EL/19 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
246 | Removal of old ,unwanted cables | Chemical Hazard | gas poisoning | Gas poisoning, Unconsiousness | All Employees concerned working in the area. | Work permit. Co level to be monitored continously if the task is carried out in Gas prone area. | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
247 | Removal of old ,unwanted cables | Chemical Hazard | Inhaling of dust while cleaning panel | personal injury, suffocation | All Employees concerned working in the area. | Use of PPE's like nose mask as per IS 9473 | 1 | 2 | 2 | Ensuring canopy is in place while doing periodic maintennace | NA | In progress | 1 | 2 | 2
248 | Removal of old ,unwanted cables | Behavioural Hazard | Hazards due to Human Error like cutting of removing wrong cable | personal injury, Equipment damage | Engineer, Electrician, Contractor | WI/ELECT/28 | 1 | 4 | 4 | Existing control measures are adequate | NA | COMPLETED | 1 | 4 | 4
249 | HT Blower Feeder capacitor current checking | Electrical Hazard | Electric shock, burns, Flashover | electrocution/burn injuries | Electrician | Electrical S/D and LOTOV, WI/EL/16, Use of arc flash suit | 2 | 2 | 4 | Usage of Arc flash suit | NA | COMPLETED | 2 | 2 | 4
250 | HT Blower Feeder capacitor current checking | Chemical Hazsard | Dust | Unconsiousness | All Employees concerned working in the area. | Use of PPE's like nose mask as per IS 9473 while cleaning outgoing feeder compartment | 1 | 2 | 2 | Ensuring canopy is in place while doing periodic maintennace | NA | In progress | 1 | 2 | 2
251 | HT Blower Feeder capacitor current checking | Behavioural Hazard | Hazards due to Human Error like Not insulating the disconnected cable. | personal injury, Equipment damage | Engineer, Electrician, Contractor | Surprise checks, WI/EL/16 | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3
252 | Providing independent electrical connection to BF2 CB5 MOTOR 1 and 2 | Safety Hazard | Hazards due to taking shutdown on drive no 1 and working on drive no 2 and vice versa. | personal injury, Equipment damage | Electrical and mechanical maintenance team , operational team and contract workman | Work instruction for CB5 BF2 motor changeover WI/EL/31 | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
253 | Providing independent electrical connection to BF2 CB5 MOTOR 1 and 3 | Safety Hazard | Hazards due to taking shutdown on only one drive and working on CB 5 conveyor belt | personal injury, Equipment damage | Electrical and mechanical maintenance team , operational team and contract workman | Work instruction for CB5 BF2 motor changeover WI/EL/31 | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
254 | Starting HBS ID on VFD or Star delta with changeover facility | Safety Hazard | Hazards due to taking shutdown on wrong SFU isolator ( Only star/ delta or only VFD without isolating main incomer SFU) | personal injury, Equipment damage | Electrical and mechanical maintenance team , operational team and contract workman | Work instruction WI/EL/ 34, Training | 2 | 2 | 4 | Existing control measures are adequate | NA | COMPLETED | 2 | 2 | 4
255 | Maintenance of HT system | Electrical Hazard | Electric shock, burns, Flashover | personal injury | Electrician | Electrical S/D and LOTOV, WI/EL/16, Use of arc flash suit | 2 | 2 | 4 | Usage of Arc flash suit | NA | COMPLETED | 2 | 2 | 4
256 | Maintenance of HT system | Chemical Hazsard | Dust | Soffocation, personal injury | All Employees concerned working in the area. | Use of PPE's like nose mask as per IS 9473 while cleaning outgoing feeder compartment | 1 | 2 | 2 | Ensuring canopy is in place while doing periodic maintennace | NA | In progress | 1 | 2 | 2
257 | Maintenance of HT system | Behavioural Hazard | Hazards due to Human Error like Not insulating the disconnected cable. | personal injury, Equipment damage | Engineer, Electrician, Contractor | Surprise checks, WI/EL/16 | 1 | 3 | 3 | Existing control measures are adequate | NA | COMPLETED | 1 | 3 | 3